## Indoor
Technical specification
U-Match Air Conditioner Indoor Unit
Parameter(Unit)
3 | Type |  |  |  | Cassette | Cassette | Cassette | Cassette | Cassette | Cassette
[5 empty] | 12K | 18K | 24K | 36K | 48K | 60K
1 | Model |  |  |  | GUD35T/A-S | GUD50T/A-S | GUD71T/A-S | GUD125T/A-S | GUD140T/A-S | GUD160T/A-S
2 | Code |  |  |  | ET010N1850 | ET010N1860 | ET010N1840 | ET010N1790 | ET010N1800 | ET010N1810
21-22-23 | Electrical Data | Power supply |  | V-Hz-Ph | 220-240-50/60-1 | 220-240-50/60-1 | 220-240-50/60-1 | 220-240-50/60-1 | 220-240-50/60-1 | 220-240-50/60-1
32 |  | Power input1 | Cooling | kW | 0.030 | 0.035 | 0.055 | 0.100 | 0.110 | 0.170
33 |  |  | Heating | kW | 0.030 | 0.035 | 0.055 | 0.100 | 0.110 | 0.170
34 |  | Input current1 | Cooling | A | — | — | — | — | — | —
35 |  |  | Heating | A | — | — | — | — | — | —
36 |  | Max. Overcurrent Protection |  | A | — | — | — | —— | JF00304012— | —
24 |  | Min/Max Voltage | Min/Max Voltage (V) | V | 198/264 | 198/264 | 198/264 | 198/264 | 198/264 | 198/264
25×27 |  | Power cord spec | Electrical Conduit Size (Inch) | mm2xpcs | 1×3 | 1×3 | 1×3 | 1×3 | 1×3 | 1×3
28 | Fuse (A) |  |  | A | 3 | 3 | 3 | 3 | 3 | 3
10/11/12 | Sound Pressure Level (H/M/L)* |  |  | dB (A) | 37/35/31 | 39/35/31 | 45/41/39 | 48/48/46/42 | 49/46/42 | 52/50/48
13/14/15 | Sound Power Level (H/M/L)* |  |  | dB (A) | —/—/— | —/—/— | —/—/— | —/—/— | —/—/— | —/—/—
96 | Refrigerant | Type |  | － | R410A | R410A | R410A | R410A | R410A | R410A
99/101 |  | Control |  | － | —/— | —/— | —/— | —/— | —/— | —/—
5 | Air Flow Volume(rated EXP) |  |  | CFM | 382/341/282/235 | 412/341/282/235 | 735/674/559/500735/674/559/500 | 883/853/795/706 | 1059/1000/883/765 | 1177/1118/942/824
4 |  |  |  | m3/h | 650/580/480/400 | 700/580/480/400 | 1250/1150/950/850 | 1500/1450/1350/1200 | 1800/1700/1500/1300 | 2000/1900/1600/1400
6 | External Static Pressure |  | Rated | Pa | 0 | 0 | 0 | 0 | 0 | 0
7 |  |  |  | InWg | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00
8 |  |  | Range | Pa | 0.0 | 0.0 | 0.00.0 | 0.0 | 0.0 | 0.0
9 |  |  |  | InWg | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00
45 | Fan Motor | Model |  | － | B-FN60C-ZL | B-FN60C-ZL | B-FN35C-ZL | FN35D-ZL | FN150A-ZL | FN150A-ZL
50 |  | Drive Type |  | － | Direct | Direct | Direct | Direct | Direct | Direct
51 |  | Speed | rpm | rpm | 700/660/560/480 | 780/660/560/480 | 580/540/460/400 | 720/700/650/560 | 700/660/580/500 | 820/780/700/630
52 |  | Power Output |  | W | — | — | — | — | — | —
49 |  | Full Load Amp(FLA) |  | A | — | — | — | — | — | —
54 |  | Capacitor |  | uF | null | — | — | — | — | —
41 | Fan | Type |  | － | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal
42 |  | Quantity |  | － | 1 | 1 | 1 | 1 | 1 | 1
44 |  | Diameter-Height |  | inch | φ12.4-6.4 | φ12.4-6.4φ12.4-6.4 | φ18.83-5.28 | φ18.83-5.28 | φ18.83-6.06 | φ18.83-6.06
61 | Evaporator | Material |  | － | Inner Groove Copper Tube-Aluminum fin | Inner Groove Copper Tube-Aluminum fin | Inner Groove Copper Tube-Aluminum fin | Inner Groove Copper Tube-Aluminum fin | Inner Groove Copper Tube-Aluminum fin | Inner Groove Copper Tube-Aluminum fin
87 |  | Face Area |  | sq.ft | 2.89 | 2.89 | 3.77 | 4.14 | 5.39 | 5.42
88 |  |  |  | m2 | 0.27 | 0.27 | 0.35 | 0.39 | 0.50 | 0.50
64 |  | Pipe Diameter |  | mm | φ7 | φ7 | φ7 | φ7 | φ7 | φ7
66 |  | Number of rows |  | － | 2 | 2 | 2 | 3 | 2 | 3
67 |  | Tube pitch(a)x row pitch(b) |  | mm | 19.05×12.7 | 19.05×12.7 | 19.05×12.7 | 19.05×12.7 | 19.05×12.7 | 19.05×12.7
71 |  | Fins per Inch(FPI) |  | － | 16 | 16 | 16 | 16 | 16 | 16
72 |  | Fin type |  | － | hydrophilic-window | hydrophilic-window | hydrophilic-window | hydrophilic-window | hydrophilic-window | hydrophilic-window
74 |  | Number of circuits |  | － | 3 | 3 | 4 | 5 | 6 | 7
75 |  | Length(L) x Height(H) x Width(W) |  | mm | 1176×228.6×25.4 | 1176×228.6×25.4 | 2037.7×171.5×25.4 | 2021×190.5×38.1 | 2021×247.7×25.4 | 2031×247.7×38.1
91 | Operation temp |  | Cooling | ℃ | ≥16 | ≥16 | ≥16 | ≥16 | ≥16 | ≥16
93 |  |  | Heating | ℃ | ≤30 | ≤30 | ≤30 | ≤30 | ≤30 | ≤30
83 | Drainage Connection Size(Outer Diameter×Wall Thickness) |  |  | mm | φ25×1.50 | φ25×1.50 | φ25×1.50 | φ25×1.5 | φ25×1.5 | φ25×1.5
95 | System Operation Control |  |  | － | Wireless Controller/Wired Controlle | Wireless Controller/Wired Controlle | Wireless Controller/Wired Controlle | Wireless Controller/Wired Controlle | Wireless Controller/Wired Controlle | Wireless Controller/Wired Controlle
112×114×116 | Dimension | Outline dimension (W×D×H) |  | mm | 570×570×265 | 570×570×570×265 | 840×840×200 | 840×840×240 | 840×840×290 | 840×840×290
124×126×128 |  | Package dimension (L×W×H) |  | mm | 698×653×295 | 698×653×295 | 943×923×245 | 963×963×325 | 963×963×379 | 963×963×379
130 | Weight | Net Weight |  | kg | 17.0 | 17.0 | 23.0 | 31.0 | 33.0 | 36.0
132 |  | Gross Weight |  | kg | 22.0 | 22.0 | 30.0 | 38.0 | 41.0 | 44.0
134 | Loading quantity (within panel) |  |  | 20'GP | 168 | 168 | 108 | 84 | 72 | 72.00
135 |  |  |  | 40'GP | 378 | 378 | 216 | 168 | 144 | 144
136 |  |  |  | 40'HQ | 432 | 432 | 240 | 192 | 144 | 144
141×143×145 | Panel | Outline dimension (W×D×H) |  | mm | 620×620×47.5 | 620×620×47.5 | 950×950×52 | 950×950×52 | 950×950×52 | 950×950×52
153×155×157 |  | Package dimension (W×D×H) |  | mm | 701×701×125 | 701×701×125 | 1033×1038×112 | 1033×1038×112 | 1033×1038×112 | 1033×1038×112
159 |  | Net Weight |  | kg | 3 | 3 | 6 | 6 | 6 | 6
161 |  | Gross Weight |  | kg | 4.5 | 4.5 | 9.5 | 9.5 | 9.5 | 9.5
Note:
1. The cooling capacity stated above is measured under following conditions : Indoor Condition: 27℃（81℉）DB/19℃（66.6℉）WB; Outdoor Condition: 35℃（95.4℉）DB/24℃（75.6℉）WB.
2. Noise is tested in the semi-anechoic room, so it should be slightly higher in the actual Operation due to environmental change.
3."1" is tested under standard condition:（请注明标准工况） "2"is tested under rated condition according to CE/Eurovent standard:（请注明CE或Eurovent标准的额定工况。）
4.* Fan different speed

## Outdoor
Technical specification
U-Match Air Conditioner Outdoor Unit
Parameter(Unit)
1 | Model |  |  |  | GUD35W/A-S | GUD50W/A-S | GUD71W/A-S | GUD125W/A-X | GUD140W/A-X | GUD160W/A-X
2 | Code |  |  |  | CF090W1550-T | CF090W1540-T | CF090W1560-T | CF090W1480-T | CF090W1500-T | CF090W1520-T
[5 empty] | 12K | 18K | 24K | 36K | 48K | 60K
4 | Indoor Unit |  | Type |  | Cassette | Cassette | Cassette | Cassette | Cassette | Cassette
5 |  |  | Model |  | GUD35T/A-S | GUD50T/A-S | GUD71T/A-S | GUD125T/A-S | GUD140T/A-S | GUD160T/A-S
6 |  |  | Code |  | ET010N1850 | ET010N1860 | ET010N1840 | ET010N1790 | ET010N1800 | ET010N1810
11 | Total Capacity |  | Cooling | kW | 3.50 | 5.00 | 7.00 | 12.02 | 14.00 | 15.00
12 |  |  |  | Btu/h | 11900 | 17000 | 23800 | 41000 | 47800 | 51200
15 |  |  | Heating | kW | 4.00 | 5.60 | 8.00 | 14.00 | 15.00 | 17.00
16 |  |  |  | Btu/h | 13600 | 19100 | 27200 | 47800 | 51200 | 58000
19/21 | EER / C.O.P |  |  | W/W | 3.40/3.64 | 3.21/3.50 | 3.21/3.64 | 2.671/3.333 | 2.8/3.409 | 2.885/3.617
20/22 |  |  |  | Btu/h.W | 11.594/12.41 | 10.936/11.94 | 10.96/12.41 | 9.114/11.373 | 9.554/11.632 | 9.842/12.341
23/24 | SEER / HSPF |  |  | Btu/h.W | 16.00/9.00 | 16.00/9.00 | 16.00/9.00 | 16.00/9.00 | 16.00/9.00 | 16.00/9.00
31 | Energy Class |  |  | － | — | — | — | — | — | —
51-52-53 | Electrical Data | Power supply |  | V-Hz-Ph | 220-240-50/60-1 | 220-240-50/60-1 | 220-240-50/60-1 | 380-415-50/60-3 | 380-415-50/60-3 | 380-415-50/60-3
64 |  | Power input1 | Cooling | kW | 1.03 | 1.56 | 2.18 | 4.50 | 5.00 | 5.20
66 |  |  | Heating | kW | 1.10 | 1.60 | 2.20 | 4.20 | 4.40 | 4.70
68 |  | Rated Power input2 | Cooling | kW | 1.80 | 2.20 | 3.68 | 4.90 | 5.80 | 6.20
69 |  |  | Heating | kW | 1.80 | 2.20 | 3.68 | 4.70 | 5.60 | 5.80
70 |  | Input current1 | Cooling | A | 4.45 | 6.78 | 9.47 | 7.60 | 8.60 | 9.00
72 |  |  | Heating | A | 4.80 | 7.007.00 | 9.56 | 7.20 | 7.60 | 8.20
74 |  | Rated current2 | Cooling | A | 9.0 | 9.5 | 16.0 | 9.0 | 11.0 | 13.0
75 |  |  | Heating | A | 9.0 | 9.5 | 16.0 | 8.2 | 10.0 | 11.0
76 |  | Max. Overcurrent Protection |  | A | — | — | — | — | — | —
54 |  | Min/Max Voltage | Min/Max Voltage (V) | V | 198/264 | 198/264 | 198/264 | 342/456 | 342/456 | 342/456
55×57 |  | Power cord spec | Electrical Conduit Size (Inch) | mm2xpcs | 1.50×3 | 1.50×1.50×3 | 2.50×3 | 1.50×5 | 1.50×5 | 1.50×5
35/36/37 | Sound Pressure Level (H/M/L)* |  |  | dB (A) | 51/—/— | 55/—/— | 56/—/— | 58/—/— | 59/—/— | 60/—/—
38/39/40 | Sound Power Level (H/M/L)* |  |  | dB (A) | 61/—/— | 65/—/— | 66/—/— | 68/—/— | 69/—/— | 70/—/—
166 | Refrigerant | Type |  | － | R410A | R410A | R410A | R410A | R410A | R410A
167 |  | Charge |  | kg | 1.00 | 1.25 | 2.00 | 3.40 | 3.7 | 3.8
169/171 |  | Throttling Method |  | － | Electronic expansion valve/Electronic expansion valve | Electronic expansion valve/Electronic expansion valve | Electronic expansion valve/Electronic expansion valve | Electronic expansion valve/Electronic expansion valve | Electronic expansion valve/Electronic expansion valve | Electronic expansion valve/Electronic expansion valve
86 | Compressor | Trademark | trademark | － | GREE | GREE | GREE | GREE | GREE | GREE
87 |  | Manufacturer | Manufacturer | － | ZHUHAI LANDA COMPRESSOR CO.,LTD | ZHUHAI LANDA COMPRESSOR CO.,LTD | ZHUHAI LANDA COMPRESSOR CO.,LTD | ZHUHAI LANDA COMPRESSOR CO.,LTD | ZHUHAI LANDA COMPRESSOR CO.,LTD | ZHUHAI LANDA COMPRESSOR CO.,LTD
88 |  | Model |  | － | QXF-A102zE190B | QXF-B141zF030F | QXFS-D25zX090H | QXFS-D32zX090C | QXFS-F428zX450I | QXFS-F428zX450I
89 |  | Type |  | － | Inverter Rotary | Inverter Rotary | Inverter Rotary | Inverter Rotary | Inverter Rotary | Inverter Rotary
90 |  | Quantity |  | － | 1 | 1 | 1 | 1 | 1 | 1
91 |  | Capacity |  | W | 3840 | 5310 | 9650 | 14800 | 16550 | 16550
92 |  | Power Input |  | W | 1023 | 1410 | 2420 | 3720 | 4060 | 4060
95 |  | Run Capacitor |  | µF(MFD) | — | — | — | — | — | —
93 |  | Rated Load Amp (RLA) |  | A | 4.6 | 7.2 | 11.7 | 7.9 | 8.2 | 8.2
94 |  | Locked rotor Amp (L.R.A) |  | A | — | — | — | — | — | —
96 |  | Thermal protector |  | － | External Auto Reset Thermal Overload Protector | External Auto Reset Thermal Overload Protector | External Auto Reset Thermal Overload Protector | — | — | —
97 |  | Crankcase | W | W | 0 | 0 | 0 | 40 | 40 | 40
98 |  | Refrigerant oil | Type | － | FW68DA or equivalent | FW68DA or equivalent | FW68DA or equivalent | FW68DA or equivalent | FW68DA or equivalent | FW68DA or equivalent
99 |  |  | Charge Volume | L | 0.28 | 0.45 | 0.95 | 0.95 | 1.35 | 1.35
34 | Air Flow Volume |  |  | CFM | 1765.5 | 1765.5 | 2119 | 3472.15 | 3472.15 | 3472.15
33 |  |  |  | m3/h | 3000 | 3000 | 3600 | 5900 | 5900 | 5900
110 | Fan Motor | Model |  | － | FW30J-ZL | LW40C-ZL | LW60M-ZL | B-SWZ150A | B-SWZ150A | B-SWZ150A
115 |  | Drive Type |  | － | Direct | Direct | Direct | Direct | Direct | Direct
116 |  | Speed (H/M/L)* |  | rpm | 860 | 860 | 820 | 820 | 820 | 820
117 |  | Power Output |  | PH | — | — | — | — | — | —
114 |  | Full Load Amp(FLA) |  | A | — | — | — | — | — | —
111 |  | Insulation class |  | － | B or E | B or E | B or E | E/B | E/B | E/B
112 |  | Safe class |  | － | IP24 | IP24 | IP44 | IP44 | IP44 | IP44
119 |  | Capacitor |  | uF | — | — | — | — | — | —
106 | Fan | Type |  | － | Axial-flow | Axial-flow | Axial-flow | Axial-flow | Axial-flow | Axial-flow
107 |  | Quantity |  | － | 1 | 1 | 1 | 1 | 1 | 1
109 |  | Diameter-Height |  | inch | φ17.2-4.56 | φ17.2-4.56 | φ20.47-6.08 | φ21.65-7 | φ21.65-7 | φ21.65-7
126 | Condenser | Material |  | － | Inner Groove Copper Tube-Aluminum fin | Inner Groove Copper Tube-Aluminum fin | Inner Groove Copper Tube-Aluminum fin | Inner Groove Copper Tube-Aluminum fin | Inner Groove Copper Tube-Aluminum fin | Inner Groove Copper Tube-Aluminum fin
152 |  | Face Area |  | sq.ft | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
153 |  |  |  | m2 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6
129 |  | Pipe Diameter |  | mm | φ7.94 | φ7.94 | φ7 | φ7.94 | φ7.94 | φ7.94
131 |  | Number of rows |  | mm | 2 | 2 | 2 | 2 | 2 | 3
132 |  | Tube pitch(a)x row pitch(b) |  | mm | 22×19.05 | 22×19.05 | 22×19.05 | 22×19.05 | 22×19.05 | 22×19.05
136 |  | Fins per Inch(FPI) |  | － | 18 | 18 | 18 | 18 | 18 | 16
137 |  | Fin type |  | － | Ripple | Ripple | Ripple | Ripple | Ripple | Ripple
139 |  | Number of circuits |  | － | 4 | 4 | 5 | 5 | 5 | 10
140 |  | Length(L) x Height(H) x Width(W) |  | mm | 745×550×38.1 | 745×550×38.1 | 1016×660×38.1 | 1154×792×38.1 | 1154×792×38.1 | 1154×792×57.15
151 | Permissible Excessive Operating Pressure for the Discharge Side |  |  | Mpa | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6
152 | Permissible Excessive Operating Pressure for the Suction Side |  |  | Mpa | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
156 | Operation temp |  | Cooling | ℃ | –15～48 | –15～48 | –15～48 | –15～48 | –15～48 | –20～48
158 |  |  | Heating | ℃ | –15～24 | –15～24 | –15～24 | –15～24 | –15～24 | –20～24
161 | Defrosting Method |  |  | － | Auto defrost | Auto defrost | Auto defrost | Auto defrost | Auto defrost | Auto defrost
162 | Isolation |  |  | － | I | I | I | I | I | I
163 | Moisture Protection |  |  | － | IPX4 | IPX4 | IPX4 | IPX4 | IPX4 | IPX4
164 | Overload Protector |  |  | － | Discharge High Temperature Protection | Discharge High Temperature Protection | Discharge High Temperature Protection | High Presser Protector Low presser protector | High Presser Protector Low presser protector | High Presser Protector Low presser protector
181×183×185 | Dimension | Outline dimension (W×D×H) |  | mm | 818×302×596 | 818×302×596 | 892×340×698 | 940×460×820 | 940×460×820 | 940×460×820
193×195×197 |  | Package dimension (L×W×H) |  | mm | 948×420×645 | 948×420×645 | 1029×458×750 | 1083×573×973 | 1083×573×973 | 1083×573×973
199 | Weight | Net Weight |  | kg | 38.0 | 41.0 | 53.0 | 90.0 | 96.0 | 100.0
201 |  | Gross Weight |  | kg | 41.0 | 44.0 | 57.0 | 102.0 | 108.0 | 112.0
203 | Loading quantity | Outdoor Unit |  | 20'GP | 96 | 9696 | 81 | 40 | 40 | 40
204 |  |  |  | 40'GP | 204 | 204 | 171 | 84 | 84 | 84
205 |  |  |  | 40'HQ | 272 | 272 | 171 | 84 | 84 | 84
206 |  | Outdoor Unit and Indoor Unit(within panel) |  | 20'GP | 54 | 54 | 37 | 24 | 22 | 22
207 |  |  |  | 40'GP | 120 | 120 | 83 | 53 | 48 | 48
208 |  |  |  | 40'HQ | 139 | 139 | 88 | 62 | 53 | 53
211 | Connection Pipe | Valve Connection Type |  | － | Screw thread joint | Screw thread joint | Screw thread joint | Screw thread joint | Screw thread joint | Screw thread joint
212 |  | Length |  | m | 5 | 5 | 5 | 5 | 7.5 | 7.5
218 |  | Gas additional charge |  | g/m | 22.0 | 22.0 | 30.0 | 35 | 50 | 50
221 |  | Outer Diameter | Liquid Pipe | Inch | 1/4" | 1/4" | 3/8" | 0.375 | 0.375 | 0.375
223 |  |  | Gas Pipe | Inch | 3/8" | 1/2" | 5/8" | 0.625 | 0.625 | 0.625
224 |  | Max Distance | Height | m | 15 | 20 | 25 | 30 | 30 | 30
226 |  |  | Length | m | 30 | 35 | 50 | 65 | 75 | 75
Note:
1. The cooling capacity stated above is measured under following conditions : Indoor Condition: 27℃（81℉）DB/19℃（66.6℉）WB; Outdoor Condition: 35℃（95.4℉）DB/24℃（75.6℉）WB.
2. Noise is tested in the semi-anechoic room, so it should be slightly higher in the actual Operation due to environmental change.
3."1" is tested under standard condition:（请注明标准工况） "2"is tested under rated condition according to CE/Eurovent standard:（请注明CE或Eurovent标准的额定工况。）
4.* Fan different speed